METHOD STATEMENT FOR CABLE LAYING & TERMINATION INSIDE SUBSTATION

Document Reference Number: EM-5000-M-2019-RA

Location: YASI S/S to BHYG S/S

Work Scope: Cable laying & Termination inside substation

Client Contract No: N 19084

Contractor is responsible to prepare method statement for each work activities with compliance to RFC drawings, standard drawings, project specification, prevailing international standards and other relevant approvals and submit it for consultant/TAQA review and approval.

This method statement guideline is prepared in good faith in line with standard engineering practices, to guide, facilitate contractors and standardize the procedural submissions. However, it does not relieve the Contractor from their contractual obligations.

Any discrepancy between this information and actual site conditions shall be verified for its correctness and suitability, as per applicable TAQA procedures and local authorities. The Contractor shall verify and confirm submissions case to case, as per applicable law and standards.

| DOCUMENT REVIEW & AUTHORISATION |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Contractor |  | APPROVAL |  |  |  |  |  |
|  |  | Contractor Project Manager | Sub-Contractor Project Manager | Site Manager | Duty Holder/ HSE Manager | Client/Client Representative |  |
| Name |  | Mr. R Sasitharan |  |  |  |  |  |
| Signature /Date |  |  |  |  |  |  |  |
| 1 | Does this document identify high risk activities? Yes / No If answer is “Yes” then risk assessment for each individual high-risk element of work shall be included. |  |  |  |  |  |  |
| 2 | Does the work scope include temporary works? Yes / No If answer to above question is “Yes” then a separate risk assessment/method statement shall be submitted for temporary works in addition to the method statement risk assessment for the main works |  |  |  |  |  |  |

|  | DISTRIBUTION |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| ORGANISATION NAME |  | NAME | POSITION | SIGNATURE | DATE |  |

Sub-Contractor  EPC Contractor  (OE) PM Consultant appointed by the Client  Client

|  | REVISION RECORD |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Revision |  |  | Date |  |  | Comments / Changes |  |
| 0 |  |  | 02/07/2025 |  |  | First issue-Generic |  |  |
|  | Field Change Notices |  |  |  |  |  |  |  |

Contents

Abbreviations Used	3

1. Purpose and Scope of Works	4

2. Programme and Constraints	5

3. Surveys and Engineering Design - Completed before start of work	6

4. Specifications & Standards	8

5. Permits and Permissions	9

6. Specific Legal Compliance	10

7. Resources & Competency	11

8. Communication	12

9. Supervision and Responsibilities	13

10. Health Impacts	14

11. Quality Control	15

12. Environmental Impacts	16

13. Methodology and Sequence of Works	18

14. Emergency Procedures	21

15. Appendices	22

16. Risk Assessments	23

17. Sign Off Sheet	24

# Abbreviations Used

| Abbreviations Used | Definition |
| --- | --- |
| ILO R164 | Occupational Safety and Heath Recommendation |
| ILO R175 | Safety and Heath in Construction |
| PPE | Personal protective equipment |
| COSHH | Control of Substances Hazardous to Health |
| OHL | Overhead Line (s) |
| UGC | Underground Cables |

# Purpose and Scope of Works

Purpose

This method statement outlines the step-by-step procedure for the laying, termination, and testing of 132kV XLPE power cables and associated fiber optic cables (FOC) inside the substations. All works shall be executed in full compliance with TAQA Specification S-CAB-INST-132 (Rev.0-2019) and Project Scope of Work: Sections 1.5.4, 1.6, 1.7, and 1.8.

Scope of work

The scope of this method statement covers all necessary activities related to the supply, laying, termination, and testing of 132kV XLPE power cables and associated fiber optic cables (FOC) within the BHYG Grid Station and YASI Substation basements as part of the TAQA N-19084 project. The scope includes the complete installation of 1,200 mm² single-core 132kV cables and 32-core fiber optic cables through concrete trenches and duct banks inside the substation premises. It encompasses the supply and fixing of cable trays, non-magnetic cleats, and fireproofing systems; implementation of water/fire seals at wall and floor penetrations; bonding and earthing of cable sheaths and accessories; GIS termination works in coordination with OEMs (Toshiba at BHYG and Siemens at YASI); and final testing and commissioning of the entire cable system in compliance with TAQA specifications and international standards. All materials, workmanship, and safety procedures shall meet the requirements defined in TAQA Specification S-CAB-INST-132 (Rev.0-2019), the project Scope of Work, and relevant IEC standards.

# Programme and Constraints

The working hours shall be in accordance with the contractual agreements for the project, governments guidelines and restrictions imposed by the local authorities.

| Duration of Works |  |  |  |  |
| --- | --- | --- | --- | --- |
| Anticipated start date: 01 Nov 25 |  | Anticipated finish date: 30 Mar 26 |  | Duration: 5 Months |
| Working Hours |  |  |  |  |
| Weekday | Start time: 6:00 AM |  | Finish time: 5:00 PM |  |
| Weekend | Start time: 6:00 AM |  | Finish time: 5:00 PM |  |
| Generic Constraints |  |  |  |  |
| Environmental: Spilling of fuel or hydraulic oil on site |  |  |  |  |
| Equipment/Plant/Machinery: Cable Rollers (Straight & Corner), Motorized Puller |  |  |  |  |
| Site Specific Constraints (to be identified by the Contractor) |  |  |  |  |
| Environmental: Identify Potential Sources of Waste: Wood, paper. Waste Segregation and Storage: Establish clearly labelled waste collection bins for different types of waste, such as recyclables, hazardous materials, and general waste. Ensure proper storage of hazardous materials in designated areas with appropriate containment measures to prevent spills or leaks. Waste Disposal and Recycling: Identify local regulations and guidelines for the disposal of different types of waste, including hazardous materials. Contract with licensed waste management companies for the proper disposal of hazardous materials and recycling of recyclable materials. Implement procedures for the safe transportation of hazardous materials to disposal facilities. Monitoring and Evaluation: Regularly monitor waste generation and disposal practices to identify areas for improvement. Conduct periodic audits to ensure compliance with waste management procedures and regulations. Dust can be produced in dry condition; as a result dust mask may be required. If required, water spray will be used to suppress dust. |  |  |  |  |
| Equipment/Plant/Machinery: Cable Rollers (Straight & Corner), Motorized Puller |  |  |  |  |
| Existing Infrastructure: The presence of any existing structures or underground elements |  |  |  |  |
| Utilities: Before starting excavation, refer the GIS drawings, as built drawings, inspect each trial pit location and identify existing underground utilities using a valid calibrated cable detector and maintain a proper record to avoid damaging live utilities |  |  |  |  |
| Access/Egress etc.: Only operatives with valid third-party training certificates will be allowed on site. The site will have designated walkways/walking routes for pedestrians and roads for vehicles, with a speed limit of 20 km/hr. Parking will be available on site for personnel. The work area will be clearly demarcated to restrict access and mitigate unauthorized entry. |  |  |  |  |

NOTE:

- Working days/times subject to TAQA/Local authority approval

- Night shift working hours subject to TAQA/Local authority approval

- Working near live TAQA asset subject to TAQA systems safety rules (SSR)

# Surveys and Engineering Design - Completed before start of work

The following factors can influence the selection of construction method and equipment:

- Terrain

- Soil condition

- Environmental and public constraints

- Accessibility to the location-equipment limitation

- Flooding & Groundwater

| Surveys | Document Reference |
| --- | --- |
| Topography Survey | In Progress |

| Design Reports/Drawings | Document Reference |
| --- | --- |
| PROPOSED 132kV CABLES BETWEEN BHYG G/S – YAS I S/S | N-19083.1 GG ¦ 7500 ¦ U ¦ 0001 |
| PROPOSED 132kV CABLES BETWEEN BHYG G/S – YAS I S/S Trail Pit | N-19083.1 GE ¦ ADTP ¦ N ¦ 0001 |

These requirements include, amongst others:

- The responsibility of conducting and reviewing risk assessments in admin areas shall lie with the admin (area) Manager.

- Risk assessment teams shall have the required experience, knowledge and training and be led by a competent team leader.

- Risk assessments must be conducted when planning or making change to an activity, operation, procedure or in the case of HSE incidents.

HSE Plan

Project Approved HSE Plan will be followed – HSE Plan No. ESPEC-HSE-D15

QA/QC Plan

- Quality Assurance Procedures - EPEC/TRANSCO_QCP_REV00 Quality Assurance (QA) ensures that all construction and installation processes conform to TAQA specifications, project requirements, and international standards by focusing on preventive actions and systematic planning. - Document Approvals - All method statements, ITPs, material submittals, and drawings must be reviewed and approved by TAQA prior to commencement of site work. - Pre-Qualification of Subcontractors and Technicians - All technicians performing termination, testing, or FOC works must be certified by manufacturers (Toshiba/Siemens). - Subcontractors must submit QA documentation showing compliance with TAQA’s vendor approval system. - Calibration Management - All testing instruments (Megger, HV test sets, OTDRs, torque wrenches) must have valid calibration certificates traceable to national standards. - Calibration logs shall be maintained and updated monthly. - Material Traceability - Cable drum numbers, FOC spools, and accessory batch numbers must be recorded and cross-referenced with delivery notes, test reports, and inspection logs. - Training and Competency - All site personnel shall be trained in TAQA HSE and quality policies. - Toolbox talks and method statement briefings will be conducted daily before start of work. - Audit and Surveillance - Internal QA audits will be conducted weekly to verify compliance with the approved procedures and identify any systemic issues. - Quality Control Procedures Quality Control (QC) ensures that the actual installation and test results meet predefined standards and tolerances through inspections, tests, and documentation. The following QC steps will be implemented: - Incoming Material Inspection - Power cables, FOC, cleats, trays, termination kits, and seals will be inspected upon delivery. - Acceptance criteria include: no physical damage, correct labeling, and valid type and routine test certificates per IEC 60840. - Installation Checks - Cable laying shall be monitored for correct bending radius, trefoil formation, and support spacing (≤300mm). - FOC conduit and cable segregation must be confirmed. - Cable identification tags shall be verified for every 5 meters. - Termination Inspection - Each termination will be inspected for cleanliness, stress cone fitting, bolt torque (using calibrated wrench), and sealing. - OEM presence and sign-off shall be mandatory. - Testing and Recording - All electrical and optical tests shall be performed in presence of TAQA or their authorized representative. - QC team shall maintain test logs including: - Insulation Resistance - HV Withstand Test - Partial Discharge Levels - OTDR and attenuation results - Non-Conformance Management - Any deviation from specifications shall trigger a Non-Conformance Report (NCR). - Root cause analysis will be conducted and Corrective Action Reports submitted to TAQA for approval. - Final QC Handover - As-built drawings, test reports, inspection checklists, and material traceability documents shall be compiled into a QA/QC dossier and submitted to TAQA for final acceptance.

# Specifications & Standards

| TAQA Specifications & Standards | Document Reference |
| --- | --- |
| Installation of 132kV XLPE Underground Power Cables | S-CAB-INST-132 (Rev.0-2019) |
| Material Specification for 132kV XLPE Cables and Accessories | S-CAB-MAT-132 |
| Civil Specification for Cable Duct Banks and Trenches | S-TR-CIVIL-CAB |

| Industry Specific Standards | Document Reference |
| --- | --- |
| Standards for Cable Trays and Supports | NEMA VE 1 / FG-1 |
| Power Cables with Extruded Insulation and Accessories for Rated Voltages of 30kV–150kV | IEC 60840:2020 |
| High-voltage Switchgear – Cable Terminations for GIS (Gas-Insulated Switchgear) | IEC 62271-209:2019 |

| TAQA HSE Standards | Document Reference |
| --- | --- |
| Occupational Health and Safety | ILO R164 |
| Safety and Heath in Construction | ILO R175 |
| Occupational Health, Safety Assessment Specification | OHSAS 18001 & ISO 45001 : 2018 |
| System Safety Rules | HSE-HS-13 |
| Procedure for selection & Provision of PPE | HSP.31 |
| COSHH | HSP.30 |

# Permits and Permissions

| Work Permits |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Permit to Dig: Required |  |  |  | Proximity to Electricity: Required (If our work is near existing electrical cables and substations) |  |  |  |
| Permit to Work (daily permit): |  |  |  | Confined Space Permit: Required (If excavation is deep) |  |  |  |
| Working under/adjacent/over utilities: Required ( if our work is involved near existing utilities) |  |  |  |  |  |  |  |
| Temporary Works Permits |  |  |  |  |  |  |  |
| Permit to Load: |  | Permit to Strike: |  |  |  |  |  |
| Permissions required to carry out the works |  |  |  |  |  |  |  |
| Tick as applicable: | Permit to Work |  | Access |  |  | Transfer |  |
| Others: N/A. |  |  |  |  |  |  |  |

| System Identification | Document Reference |
| --- | --- |
| noted & will provide necessary documents during execution of the work |  |

| Equipment/Tools | Certificate/Reference |
| --- | --- |
| Sand-cone apparatus | Will be submitted prior to commencing the activity |
| Calibration sand (Silica Sand) | N/A |
| Balance | N/A |
| Tools for excavating test hole (Plastic bag, bottles, scoop, chisel, measuring tape etc.) | N/A |
| Container for soil sample | N/A |

The Contractor shall provide up-to-date No Objection Certificates (NOCs) from any relevant authority or utility.

| SN | Authority/Utility | PTW required |
| --- | --- | --- |
| 1 | ADDC-TAQA Distribution | YES |
| 2 | ADNOC | YES |
| 3 | Dolphin Energy | YES |
| 4 | Du Telecom | NO |
| 5 | Etihad Rail | YES |
| 6 | Etisalat Telecom | No |
| 7 | GHQ Military Works and Telecom | No |
| 8 | ITC Right-of-Way | YES |
| 9 | MCC Monitor and Control | No |
| 10 | TWS Sewerage AD | YES |
| 11 | Tabreed Cooling | No |
| 12 | Transco Infrastructure Services | YES |

# Specific Legal Compliance

| Activity | Document Reference |
| --- | --- |
| Transport of equipment on site | ILO R164 / ILO R175/HSE-HS-13 |
| Unloading equipment | ILO R164 / ILO R175/HSE-HS-13 |

| HSE Activity | Document Reference |
| --- | --- |
| Load handling equipment | ILO R164 / ILO R175/HSE-HS-13 |
| Manual handling | ILO R164 / ILO R175/HSE-HS-13 |

# Resources & Competency

|  |  |  | Labour / Trades requirements | Numbers |  |
| --- | --- | --- | --- | --- | --- |
| 1 |  | Supervisor /Competent Person |  | 1 |  |
| 2 |  | Engineer |  | 1 |  |
| 3 |  | Cable Jointers / Termination Technicians |  | 1 |  |
| 4 |  | Fiber Optic Technician |  | 1 |  |
| 5 |  | Test Engineers |  | 1 |  |
| 6 |  | Electrician / Skilled Worker |  | 6 |  |
|  |  |  | Plant and Equipment |  |  |
| 1 |  | Cable Drum Jacks with Spindle Shaft |  | 1 |  |
| 2 |  | Motorized Cable Drum Stand (Hydraulic) |  | 1 |  |
| 3 |  | Cable Rollers (Straight/Corner Types) |  | 1 |  |
| 4 |  | Digital Tension Meter / Dynamometer |  |  |  |
|  |  |  | Materials |  |  |
| 1 |  | Chain Block & Pulley |  |  |  |
| 2 |  | Manual Trolleys |  |  |  |

| PPE |  |
| --- | --- |
| Mandatory: - Gloves - Hard hat - Safety footwear - High visibility vest/jacket Additional when required: - Safety glasses/goggles - Ear defenders | Specialist: |
| Additional site-specific PPE |  |
| The Contractor is responsible for identifying and providing any additional site-specific PPE that is required to safely complete the works. The list of identified PPE shall be included in the table below |  |

|  | Mandatory Training & Competency Requirements |  |  |
| --- | --- | --- | --- |
| Position |  | Requirements |  |
| Competent Person |  | TAQA SSR Competency Assurance Guidance Booklet No.2(SSR Summary for Contractors’ CP) Revision 1 1st January2022 HSEQ Department, TAQA |  |
| Authorized Person |  |  |  |
| HSE Engineer |  | TAQA Contractor HSE Engineer – Job Description Rev 0 |  |
| Contractor HSE Manager |  | TAQA Contractor HSE Manager – Job Description Rev 0 |  |
| Contractor HSE Officer |  | TAQA Contractor HSE Officer – Job Description Rev 0 |  |
| Site Manager / Site Engineer |  | SSR Competency Assurance Guidance Booklet No.2(SSR Summary for Contractors’ CP) Revision 11stJanuary2022HSEQ Department, TAQA |  |
| Supervisory Staff / Foreman |  | Follow TAQA requirements* |  |
| General Operative |  | Follow TAQA requirements* |  |
| Plant Operator |  | Follow TAQA requirements* |  |

*Any additional requirements to be added by TAQA as part of contractual agreements

# Communication

| Prior to commencing on works | Requirements |
| --- | --- |
| Sub-Contractor pre-start safety meeting | Always, Records required |
| On-site safety induction | Always, Records required |
| On site - competency checks prior to commencing work / QA systems | Always, Records required |

| Routine communication processes | Requirements |
| --- | --- |
| Work crews briefed on RAMS documentation | Sign off required |
| Applicable Toolbox talks (Safety / Environmental / Quality) | Sign off required |
| Contractor safety / progress meetings | Minutes of meeting |
| Workplace safety committee meetings | Minutes of meeting |
| Emergencies | Requirements |
| Emergency response actions identified and communicated | Records required |
| Accident and incident / Near Miss procedures explained | Records required |
| Task specific communication processes | Requirements |
| Follow instruction at all times from the site manager / supervisor relating to all excavation works. | Throughout duration of the works |
| Key Interfaces | Requirements |
| The Contractor shall identify key interfaces additional to the ones identified below: - TAQA - The Contractor - The Subcontractor (if any) Project meetings shall be held regularly. | Throughout duration of the works, Minutes of meeting |
| Subcontractor relationships and overall communication | Requirements |
| The Contractor shall develop a safety and overall communication plan with all Subcontractors. The details shall be provided below: A two-way daily communication shall be maintained through daily progress reports, toolbox talks, safety briefings, site visits. Etc. All the HSEQ related issues shall be discussed & communicated through weekly HSEQ review meetings & process issues shall be addressed through progress review meetings. Changes required on the method statement shall be notified immediately for the consideration of HSEQ | Where required |
| Rectification & Amendments | Requirements |
| In case of any damage, discrepancy, or change, the contractor shall bring this to the notice of the Consultant or TAQA Engineer and shall proceed further after getting necessary approval from the client. | Yes, records required |

# Supervision and Responsibilities

As a minimum, the Contractor shall undertake the following roles and responsibilities. Any additional site-specific roles that are identified as part of this method statement shall be listed in the table below, with responsibilities:

| Responsibilities | Supervisory Role |
| --- | --- |
| Responsible for execution of the contract and liaison with the Client | Site Agent / Manager |
| Responsible for carrying out daily and process checks | Competent Person / Manager |
| Responsible for the over-all direction, monitoring, coordination, control and supply of required manpower & equipment etc. of all the construction activities and related to the defined scope of work. | Project Manager |
| Responsible for the overall implementation and monitoring of all the activities involved in defined scope of work. | Construction Manager |
| Responsible for the necessary quality assurance and control, documentation, inspections and tests as per TAQA specifications. | QA/QC Engineer |
| Directly involved in the planning and execution of the activities involved in the defined scope of work. They shall be responsible for the preparation of work plan, Safety Action Plan for work permits, if required, prior to the commencement of any work. | Site Engineer |
| Responsible for marking the exact test points along the cable route using GPS or total station, ensuring accurate chainage, offset, and coordinates are recorded as per approved drawings and testing intervals. | Surveyor |
| Certified by OEMs such as Toshiba or Siemens and approved by TAQA, are responsible for executing high-voltage XLPE cable jointing and GIS terminations. Their tasks include the installation of stress cones, epoxy bushings, sheath bonding, and ensuring correct torqueing and sealing. They coordinate closely with OEM representatives during GIS interface work. | Cable Jointers and Termination Technicians |
| Responsible for the installation, splicing, and testing of 32-core fiber optic cables. This includes the placement of FOC inside conduits, termination at panels, and performing OTDR testing to ensure signal integrity and attenuation compliance. All splicing and testing records are to be documented and submitted. | Fiber Optic Technician |
| Responsible for conducting insulation resistance (IR), high-voltage AC withstand, partial discharge, and relay coordination tests. They operate test equipment, verify calibration status, and ensure that all test results are accurately logged and approved by TAQA representatives. | Test Engineers |
| Assist in all installation-related activities such as laying cables in trays or trenches, installing cable cleats and identification tags, terminating control cables, applying fireproof coatings, and connecting earthing systems. They work under the supervision of engineers and must comply with all safety instructions. | Electricians and Skilled Workers |
| Oversees the installation of mechanical supports, cable trays, trench construction, and sealing works. They coordinate between civil workers and electrical teams to ensure timely and accurate installation of all tray supports, duct entries, and fire sealing systems. | Civil/MEP Supervisor |
| Responsible for reviewing work hazards prior to the start of the work and preparing the Safe Work Plan and work permit, if required, prior to submittal to client that must be implemented and observed during works. He must observe compliance of all safety requirements as per works procedures and HSE plan, during works | Safety Engineer |
| Daily and Process Checks |  |
| Checks to be completed (to be identified by Contractor) | Required (Y/N) |
| Method Statement Approved | Y |
| Obtaining NOCs & Permits | Y |
| Obtaining existing utilities information | Y |
| Shop Drawing & Method Statement Approval | Y |
| Valid Certificate for Equipments | Y |
| Physical Conditions of Equipments | Y |

# Health Impacts

| Health Impact | Applicable (y) | Health Impact |  | Applicable (y) |  |
| --- | --- | --- | --- | --- | --- |
| Toxicity | N/A | Aspiration hazard/Asthma | N/A |  |  |
| Skin Irritation/Dermatitis | N/A |  |  |  |  |
| Eye Irritation | N/A |  |  |  |  |
| Respiratory issues | N/A |  |  |  |  |
| Carcinogenetic | N/A |  |  |  |  |
| Reproductive toxicity | N/A |  |  |  |  |
| COSHH Impacts |  |  |  |  |  |
| Substances or materials |  | COSHH assessment required |  |  |  |
| Liquids - (Toxic/Corrosive/Flammable/Explosive/Environment dangerous/Irritant/Slip hazard) |  | Not Applicable |  |  |  |
| Gases - (Toxic/Flammable/Explosive/Environment Dangerous/Irritant) |  | Not Applicable |  |  |  |
| Dust - (Explosion/Irritant/Allergic Issues) |  | Not Applicable |  |  |  |
| Fumes - (Toxic/Irritant/Suffocation/Explosive) |  | Not Applicable |  |  |  |
| Vapor - (Toxic/Irritant/Suffocation) |  | Not Applicable |  |  |  |

# Quality Control

The Contractor shall provide key contact details in the table below.

| Name of Site Manager | Telephone Number |
| --- | --- |
| Mr. Abdul Mohsin | +971 58 962 4466 |
| Name of Competent Person | Telephone Number |
| Mr. Jayateja Podili | +971 55 380 1958 |
| Name of Contract Manager | Telephone Number |
| Mr. R Sasitharan | +971 52 851 0425 |
| Name of Person Monitoring Safety | Telephone Number |
| Mr. Mujahid Abbas | +971 54 998 4915 |
| Name of Client Contact | Telephone Number |
| Name of First Aider | Telephone Number |
| Mr Najeerullah | +971 52 509 0552 |
| Name of Fire Warden | Telephone Number |
| Mr Najeerullah | +971 52 509 0552 |
| Additional Roles |  |
| Role | Telephone Number |
| Mr. Yousef Sulaiman, Project Manager | +971 52 509 0560 |

Project Inspection & Test Plan to be provided by the Contractor, and to contain (at a minimum) the information displayed in the table below.

| Programmed Works | Inspection/Test Activity | Specification Reference | Document Reference | Personnel | Date of Inspection/Test |
| --- | --- | --- | --- | --- | --- |
| Drawing Approval | Document Review | S-CAB-MAT-132 | TAQA Spec. |  |  |
| Method Statement Approval | Document Review | S-CAB-INST-132 (Rev.0-2019) | TAQA Spec. |  |  |
| Equipment Calibration Check | Document Review | S-TR-CIVIL-SOIL | TAQA Spec. |  |  |
| Material Receipt | Document Review | S-CAB-MAT-132, PO, Packing List | TAQA Spec. |  |  |
| Storage & Handling | Ensure drums stored upright, under cover, | S-CAB-INST-132 (Rev.0-2019) | TAQA Spec. |  |  |
| Cable Tray & Support Installation | Verify support spacing, alignment, NEMA rating | DWG TR CAB 01 27 01, S-CAB-INST-132 | TAQA Spec. |  |  |
| Cable Pulling (Power & FOC) | Check trefoil formation, tension monitoring, roller spacing, and pulling direction | S-CAB-INST-132 (Rev.0-2019),Manufacturer Instructions | TAQA Spec. |  |  |
| Termination (GIS) | OEM specialist termination, epoxy bushing, | S-CAB-INST-132 (Rev.0-2019), IEC 62271-209, Manufacturer Manual | TAQA Spec. |  |  |
| FOC Splicing & Testing | OTDR trace, attenuation, and continuity testing | S-CAB-INST-132 (Rev.0-2019), IEC 60794, | TAQA Spec. |  |  |
| HV Testing (Power Cable) | IR, AC withstand (170kV for 15 min), partial discharge test | S-CAB-INST-132 (Rev.0-2019), IEC 60840:2020 | TAQA Spec. |  |  |
| Protection Relay Testing | End-to-end relay checks (Siemens 7SD522, Toshiba GRL100), CT/VT wiring | S-CAB-INST-132 (Rev.0-2019), TAQA Protection Manual |  |  |  |

# Environmental Impacts

| H&S References |  |  |
| --- | --- | --- |
| ILO R130-Hygiene recommendation |  |  |
| ILO R175-Safety and Health in Construction |  |  |
| HSE-HS-13-Safety Rules (TAQA) |  |  |
| COSHH HSP.30 |  |  |
| Site Access Notes and Special Arrangements: |  |  |
| - Full time Coaster bus available at site with Air Conditioning in ON position - Mobile Toilet - Individual water bottles - 20 liters cool water Thermos - Fire Extinguisher |  |  |
| Site Storage Facilities |  |  |
| General Storage Requirements - All materials, equipment, and plant must be stored securely to prevent theft and damage. Use covered or enclosed storage areas to protect materials from adverse weather conditions. Hazardous Materials - Store hazardous materials in designated areas with appropriate containment measures to prevent spills or leaks. - Clearly label all hazardous materials and their storage areas. - Keep SDS for all hazardous materials on-site and accessible to all relevant personnel. Waste Management - Establish clearly labelled waste collection bins for different types of waste (e.g., recyclables, hazardous materials, general waste). - Ensure proper storage of waste materials to prevent contamination and environmental hazards. Equipment and Tools Storage - Use lockable containers or storage units for small tools and equipment to prevent theft. |  |  |
| Waste Removal Arrangements |  |  |
| Waste Skip shall be provided as per Tadweer requirements. |  |  |
| Security Arrangements |  |  |
| - Security guards will be deployed to ensure 24/7 site security, controlling access, and preventing theft, vandalism, and unauthorized entry. - A properly secured, monitored storage facility will be provided on site for hand tools, equipment etc. |  |  |
| Management of Change at Site |  |  |
| - Management of change procedure by TAQA – Note for TAQA: To be developed by TAQA if not available. Note: - Changes can have an impact on HSE at work. These may include temporary works or works omitted from the original method statement. - The control measures for the management of change should include risk assessment, effective coordination and cooperation between all parties involved. These changes should be recoded and signed by all parts involved. |  |  |
| Special Emergency Procedures |  |  |
| - Emergency Medical/First Aid response - Access and Egress plans Environmental damage - Injuries to the employees and general public |  |  |
| Environmental Impact |  |  |
| - Spill control – with spill kits available on site. (Diesel, petrol or hydraulic oil) - Appropriate fuel storage - Appropriate fire prevention |  |  |

# Methodology and Sequence of Works

Employers Requirements

Pre-Requisite - Availability of approved location drawings and Ground Investigation Specifications. - All the procedures as defined on the Quality Inspection Plan & Checklist shall be followed. - Prior to the commencement of the main work, necessary & relevant clearances / RFI / - Approvals shall be obtained from Consultant/TAQA and other concerned authorities. - Verify site condition - Check all environmental constraints and public constraints - Check the accessibility to the site and choose the prefer method of boring. - Ensure the equipment certification is available and within validity period - Check equipment and tools required for the works. Ensure that all equipment’ certificates are available and within the validity period (inspection and maintenance records) - All available options for construction techniques and equipment with respect to the specific site conditions are reviewed and evaluated. - Site personnel are identified fulfilling TAQA competency requirements Where necessary, security and Welfare provision are established - The working areas and sites boundaries are clearly up defined and secured Construction & Installation - Security and Welfare provision are established - The working areas and sites boundaries are clearly up defined and secured - Transport of the equipment at site Cable Laying - IFC drawings, permits, and routing to be confirmed. - Store drums properly; lift with jacks/cranes; no dragging. - Install cable trays/ladders with proper spacing and earthing. - Cable Pulling – Use rollers and guiding tools; maintain bending radius; avoid damage. - Separate LV, MV, and control cables as per standards. - Label cables clearly at both ends. - Testing – IR, continuity, hi-pot before termination. Cable Termination - Terminate in dry, dust-free area. - Cut and strip cable ends carefully. - Use approved kits; follow manufacturer instructions. - Crimping & Torque – Use calibrated tools for lugs/bolts. - Earthing – Bond shields and armor properly. - Inspection & Testing – Perform and document all tests before energization.

Sequence of Work

- Prior Activities - Sequence of Works

Method Statement

This methodology prepared as per the TAQA specification S-CAB-INST-132 (Rev.0-2019); - Preparatory Activities - Before mobilization, TAQA NOC and PTW must be obtained. Site entry permits and any temporary shutdown requests will be arranged in coordination with the Substation O&M team. - The route inside the substation basement shall be confirmed with reference to approved drawings (DWG TR CAB 01 00 05). The actual path will be marked physically and verified via GPS at every 10-meter interval to ensure accuracy of layout and later support as-built documentation. - All cable drums, trays, cleats, sealing materials, and termination kits shall be received and inspected. Cable drums will be checked for physical integrity, correct labeling, and availability of manufacturer’s test certificates in accordance with IEC 60840:2020. - Fireproofing systems and mechanical sealants will be verified to ensure TAQA approval and IP68 compliance. - Cable trenches and duct banks shall be prepared as per S-TR-CIVIL-CAB. Concrete works will include 75mm clear cover on all sides and tanking waterproofing on buried portions. Internal trench routes shall be cleaned and confirmed free from debris or sharp protrusions. - Cable Laying Works - Cable Tray and Support Installation - Galvanized steel cable trays will be installed along the predefined routes, using mechanical fixings at 1m intervals. Tray sizes and layout will follow NEMA 3/5/7 ratings. Vertical separation between trays will be maintained at 300mm minimum to allow ventilation and safe cable bending. - Cable Pulling and Laying - XLPE cables will be pulled using powered rollers (≤2m spacing) and anti-friction rollers at bends. Maximum pulling tension shall not exceed 15 kN/m². Directional rollers will be used at turning points. - Cables will be laid in trefoil formation with vertical snaking provided at termination ends, in accordance with OEM design to accommodate thermal expansion. - FOC will be pulled in pre-installed 100mm diameter high-impact PVC conduits placed parallel to HV cables but isolated to prevent electromagnetic interference. - Intermediate Fixing - Non-magnetic trefoil cleats will be fixed at ≤300mm intervals to secure the cables. Cable identification tags and direction arrows will be placed at every 5m. - Backfilling and Cable Protection - Where cables are buried (if applicable), thermal backfill sand (with resistivity ≤120 cm°C/W) will be laid in 150mm compacted layers above and below the cables. Warning tapes will be installed 300mm above the cable trench. - Termination and Sealing Works - GIS Termination Interface - Termination kits and stress cones will be installed under the supervision of Toshiba (BHYG) and Siemens (YASI) OEM engineers. SF₆ compartments will be isolated and degassed prior to installation. - Epoxy bushings, stress cones, and connection flanges will be installed using calibrated torque tools. If required, non-linear resistors will be mounted as per OEM instruction manuals and IEC 62271-209:2019. - Fire and Water Sealing - Cable entries through walls and floors will be sealed using TAQA-approved mechanical seals (e.g., Hauff-Technik or Roxtec), ensuring IP68 rating. - Fire-retardant mastic and coatings will be applied externally over cables at duct entries, in accordance with the manufacturer’s fire rating certification. - Earthing and Bonding - Coaxial bonding cables will connect each cable sheath to the link boxes. Earth continuity will be established by connecting all metal trays and supporting hardware to the substation grounding mesh using 50mm² tinned copper earth wires. - Earthing resistance at the link box will be confirmed to be ≤5 ohms through loop impedance testing. - Testing and Commissioning - Electrical Testing - Insulation Resistance: Power cables will be tested with a 5kV Megger, requiring a minimum of 1,000 MΩ. - HV AC Test: Cables will be subjected to 170kV for 15 minutes as per IEC 60840. - Partial Discharge: PD testing shall confirm discharges <10 pC at operating voltage. - FOC Testing - Optical fiber attenuation will be measured at both 1310nm and 1550nm using an OTDR. End-to-end insertion loss must be within acceptable limits (<0.35 dB/km for single mode). - Protection Relay Testing - End-to-end communication and protection function testing shall be performed using secondary injection on the Siemens 7SD522 and Toshiba GRL100 relays, simulating faults and confirming relay coordination. - As-Built Documentation - All test records, final cable routes (including GPS coordinates), and termination details will be documented. Marked-up drawings shall be converted to final as-built versions and submitted to TAQA for recordkeeping.

Verification/Validation pause points

Equipment Calibration Check – Verify calibration certificates before testing. Test Location Verification – Mark and confirm locations as per drawings. Layer Readiness Confirmation – Ensure compaction is completed before testing. Compaction Result Review – Pause if % compaction < 95% MDD; apply corrective action.

Lifting plan arrangement

Not Applicable for this Activity

| Testing and Commissioning – Not Applicable – No HV/LV Equipment |  |
| --- | --- |
| TAQA Approved Personnel | Standard Test Equipment ID No. |

# Emergency Procedures

| Hospital (A & E) |  |
| --- | --- |
| NMC Royal Hospital-Khalifa City | 8001122 |
| Burjeel Medical Centre Al Zeina-Al Raha | 025506691 |
| Yas Marina Circuit Medical Centre | 026599800 |
| Emergency Contact Numbers |  |
| Emergency / Police / Fire / Ambulance | Police-999, Fire- 997, Ambulance-998 |
| First Aid Appointed Persons on site | Mr Najeerullah |
| First Aid Equipment | First Aid Box |
| Marine Emergencies | 996 |
| In case of damage to any of the services listed below, use the numbers listed to report the damage: |  |
| TAQA | 024164207 |
| Electricity | 991 |
| Water | 992 |

# Appendices

Document/Drawings/Reports/etc.

- Risk Assessment

# Risk Assessments

|  | Risk Assessments |  |
| --- | --- | --- |

| Prepared by: Site Engineer/Competent Person | Reviewed by: EHS Engineer/ Site Manager | Approved by: Project Manager/Site Manager | Consultant Approval |
| --- | --- | --- | --- |
| Jayateja Podili |  |  |  |

# Sign Off Sheet

| Name | Signature | Company | Date |
| --- | --- | --- | --- |